## Sheet1
Pr | 8 | Prantl number water ~ 60°F
mu | 0.00108 | N s /m2
specific volume water | 0.001 | m3/kg
kinematic viscosity | 1.08e-06 | m2/s
Outer Diameter Coil Tube | 0.625 | in
Wall thickness | 0.02 | in
Inner Diameter Coil Tube | 0.585 | in
| 0.014859 | m
Thermal conductivity water | 0.59 | W/m-K
Velocity (fps) | Velocity (m/s) | Re | NuD | h (W/m2-K) | dh/dV (W/m2-K) / (m/s)
1 | 0.3048 | 4193.54 | 41.7858 | 1659.17 | 4354.777
1.25 | 0.381 | 5241.925 | 49.9524 | 1983.4392 | 4164.7018
1.5 | 0.4572 | 6290.31 | 57.7965 | 2294.9007 | 4015.5743
1.75 | 0.5334 | 7338.695 | 65.3821 | 2596.0995 | 3893.6625
2 | 0.6096 | 8387.08 | 72.7533 | 2888.7828 | 3791.0535
2.25 | 0.6858 | 9435.465 | 79.9419 | 3174.2191 | 3702.7928
2.5 | 0.762 | 10483.85 | 86.9722 | 3453.3683 | 3625.5835
2.75 | 0.8382 | 11532.235 | 93.863 | 3726.9799 | 3557.1271
3 | 0.9144 | 12580.62 | 100.6295 | 3995.6542 | 3495.7605
3.25 | 0.9906 | 13629.005 | 107.284 | 4259.8821 | 3440.244
3.5 | 1.0668 | 14677.39 | 113.8369 | 4520.0717 | 3389.6301
3.75 | 1.143 | 15725.775 | 120.2966 | 4776.5674 | 3343.1792
4 | 1.2192 | 16774.16 | 126.6708 | 5029.663 | 3300.3038
4.25 | 1.2954 | 17822.545 | 132.9657 | 5279.6123 | 3260.5295
4.5 | 1.3716 | 18870.93 | 139.1869 | 5526.6365 | 3223.4684
4.75 | 1.4478 | 19919.315 | 145.3394 | 5770.9296 | 3188.7994
5 | 1.524 | 20967.7 | 151.4274 | 6012.6634 | 3156.2538
5.25 | 1.6002 | 22016.085 | 157.4548 | 6251.9909 | 3125.6047
5.5 | 1.6764 | 23064.47 | 163.425 | 6489.0488 | 3096.659
5.75 | 1.7526 | 24112.855 | 169.3412 | 6723.9607 | 3069.2506
6 | 1.8288 | 25161.24 | 175.2062 | 6956.838 | 3043.2362
6.25 | 1.905 | 26209.625 | 181.0225 | 7187.7821 | 3018.4912
6.5 | 1.9812 | 27258.01 | 186.7924 | 7416.8855 | 2994.9063
6.75 | 2.0574 | 28306.395 | 192.5181 | 7644.2329 | 2972.3857
7 | 2.1336 | 29354.78 | 198.2015 | 7869.902 | 2950.8444
7.25 | 2.2098 | 30403.165 | 203.8444 | 8093.9645 | 2930.2071
7.5 | 2.286 | 31451.55 | 209.4486 | 8316.4868 | 2910.4066
7.75 | 2.3622 | 32499.935 | 215.0155 | 8537.5302 | 2891.3827
8 | 2.4384 | 33548.32 | 220.5466 | 8757.1519 | 2873.0813
8.25 | 2.5146 | 34596.705 | 226.0433 | 8975.4049 | 2855.4537
8.5 | 2.5908 | 35645.09 | 231.5067 | 9192.339 | 2838.4558
8.75 | 2.667 | 36693.475 | 236.9381 | 9408.0005 | 2822.0474
9 | 2.7432 | 37741.86 | 242.3385 | 9622.4331 | 2806.1922
9.25 | 2.8194 | 38790.245 | 247.709 | 9835.6774 | 2790.8569
9.5 | 2.8956 | 39838.63 | 253.0506 | 10047.7721 | 2776.0111
9.75 | 2.9718 | 40887.015 | 258.3641 | 10258.7533 | 2761.6268
10 | 3.048 | 41935.4 | 263.6504 | 10468.6551 | 2747.6785
10.25 | 3.1242 | 42983.785 | 268.9104 | 10677.5099 | 2734.1425
10.5 | 3.2004 | 44032.17 | 274.1447 | 10885.3483 | 2720.997
10.75 | 3.2766 | 45080.555 | 279.3542 | 11092.1993 | 2708.2218
11 | 3.3528 | 46128.94 | 284.5395 | 11298.0903 | 2695.7982
11.25 | 3.429 | 47177.325 | 289.7013 | 11503.0474 | 2683.7089
11.5 | 3.5052 | 48225.71 | 294.8402 | 11707.0956 | 2671.9378
11.75 | 3.5814 | 49274.095 | 299.9568 | 11910.2584 | 2660.4699
12 | 3.6576 | 50322.48 | 305.0517 | 12112.5585 | 2649.291
12.25 | 3.7338 | 51370.865 | 310.1254 | 12314.0174 | 2638.3882
12.5 | 3.81 | 52419.25 | 315.1784 | 12514.6556 | 2627.7492
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Coil manufacturers recommend speeds > 2.5 because this is the transition to turbulent flow, as evidenced by this Reynolds number calculation

## Sheet2
Example Coil
1st floor 1P-6
Air flow | 11700 | CFM
Entering Air Temp | 76 | °F
Leaving Air Temp | 56 | °F
Entering Air Wetbulb | 63.5 | °F
Entering Air Specific Volume | 13.7135 | ft³/lb
Air specific volume | 13.5 | ft³/lb
Specific Heat Air | 0.24 | BTU/lb-°F
Mass flow rate | 51190.4172 | lb/hr
Water flow | 49 | gal/min
Specific Heat Water | 1 | BTU/lb-°F
Water density | 62.4 | lb/ft³
Water density | 8.3417 | lb/gal
Water entering temp | 45 | °F
Water leaving temp | 57 | °F
Water mass flow rate | 24524.4999 | lb/hr
Air energy | 245714.0025 | BTU/hr
Water energy | 294293.9992
Air Capacity | 12285.7001 | BTU/°F
Water capacity | 24524.4999 | BTU/°F

## Air Side h
Entering Air Dry Bulb | 81 | °F
| 27.2222 | °C |  |  | Property |  | Air | Water |  | Rows | 1/2" tube | 5/8" tube
Entering Air Wet Bulb | 68 | °F |  |  | Pr |  | 0.733 | 8 |  | 1 | 5.5 | 5.5
| 20 | °C |  |  | mu | N s /m² | 1.846e-05 | 0.00108 |  | 2 | 6.5 | 6.5
Entering Air w* | 0.014695 |  |  |  | specific volume | m³/kg |  | 0.001 |  | 3 | 6.5 | 6.5
Entering Air w | 0.011674 |  |  |  | kinematic viscosity | m²/s |  | 1.08e-06 |  | 4 | 6.5 | 7.5
Entering Air Partial Pressure | 0.27077 | psia |  |  | Thermal Conductivity | W/m-K |  | 0.59 |  | 5 | 7.5 | 8.75
Entering Air Enthalpy | 32.2463 | BTU/lb |  |  | Specific Heat | J/kg-K | 1007 | 4189 |  | 6 | 8.5 | 10
| 75004.9282 | J/kg | [7 empty] | 8 | 10.5 | 12.5
Entering Air Dew Point Temperature | 61.5924 | °F | [7 empty] | 10 | 13 | 15
| 16.4402 | °C | [7 empty] | 12 | 15 | 17.5
Entering Water Temperature | 45 | °F
| 7.2222 | °C
Sat. Partial pressue @ Water Ent. Temp | 0.14755 | psia
Sat. Air Enthalpy @ Water Ent. Temp | 17.6187 | BTU/lb
| 40981.0876 | J/kg
Water flow, GPM | 100 | GPM
| 0.006309 | m³/s
Mass flow rate, water | 6.309 | kg/s
Air Volumetric Flow Rate | 12000 | CFM
| 5.6634 | m³/s
Air density | 1.225 | kg/m³
Specific heat air | 1007 | J/kg-K
Mass flow rate, air | 6.9376 | kg/s
| 55061.461 | lbm/hr
Fin thickness | 0.008 | in
| 0.0002032 | m
Fins per inch | 8 | fins/in
Fin spacing | 0.117 | in
| 0.0029718 | m
Tube thickness | 0.02 | in
| 0.000508 | m
Tube Material | Copper
Copper thermal conductivity | 385 | W/m-K
Aluminum thermal conductivity | 237 | W/m-K
Number of Rows | 6 | Count
Number of Tubes/Row | 28 | Count
Number of Tubes | 168 | Count
Tube OD | 0.625 | in
| 0.015875 | m
Tube Outer Radius | 0.3125 | in
| 0.0079375 | m
Tube Outer Area | 0.00019793 | m²
Tube ID | 0.585 | in
| 0.014859 | m
Tube Inner Area | 0.00017341 | m²
Water Velocity | 1.2994 | m/s
| 4.263 | fps
Water Re | 17877.2467
Water Nu | 133.2921
Water h | 5292.5719 | W/m²-K
Internal Thermal Resistance, Ri | 1.1292e-05 | K/W
Distance between tube rows | 1.6667 | in
| 0.042333 | m
Percent fins | 0.064
Percent non-fin | 0.936
Ap | 16.7325 | m² | Equation 77, Area of exposed tube
As | 319.4883 | m² | Equation 78, Fin area
Ao | 336.2209 | m² | Equation 79, Total air side heat transfer area
Am,f | 1.2428 | m² | Min cross-sectional area: This accounts for the cross-sectional area of the tubes
Ai,w | 16.7325 | m²
Coil Height | 42 | in
| 1.0668 | m
Coil Width | 84 | in
| 2.1336 | m
Coil Depth | 10 | in
| 0.254 | m
Equivalent Fin Diameter | 1.7841 | in
| 0.045317 | m
Equivalent Fin Radius | 0.89206 | in
| 0.022658 | m
Fin Length | 0.57956 | in
| 0.014721 | m
Total # of Fins | 672
Hydraulic Diameter | 0.0037554 | m | From Dissertation:
| 0.14785 | in
Air Velocity | 4.5571 | m/s
| 897.0621 | ft/min
Fin thickness/Hydraulic Diameter | 0.054109
Fin thickness/Fin length | 0.013804
Fin spacing/Fin length | 0.20188
Fin Diameter, eq/Distance between tube rows | 1.0705
Fin thickness/Fin spacing | 0.068376
C1 | 0.10507
C2 | -0.3342
Reynolds Number | 1135.66
Stanton Number | 0.012312
Dry heat transfer coefficient, h | 69.2117 | W/m²-K
Adjusted wet heat transfer coefficient, h | 82.0166 | W/m²-K
Wall Resistance, Rm | 7.8857e-08 | K/W
Wall Resistance calc 2, Rm | 7.6278e-08 | K/W
ρ = Dfin/Dtube | 2.8546
fai | 0.78923
ue | -0.42555
ub | -1.2148
Numerator | #NUM!
Denominator
Dry
m (Dry) | 53.6128 | 1/m | See Incropera pg. 151
C2 (circular fin) | 0.65743
m r1 | 0.42555
m r2 | 1.2148
Fin Numerator | 1.3797
Fin Denominator | 1.2148
Dry Fin efficiency | 0.74668
Dry Overall efficiency | 0.75928
Wet
m (Wet) | 58.3619 | 1/m
C2 (circular fin) | 0.60393
m r1 | 0.46325
m r2 | 1.3224
Fin Numerator | 1.4042
Fin Denominator | 1.1868
Wet Fin Efficiency | 0.71453
Wet Overall Efficiency | 0.72874
All Cases
Sum of Constant Resistances (Rm + Ri + Rf) | 1.1368e-05 | K/W
a | 19927.6793 | J/kg
b | 2707.5994 | J/kg-K
[9 empty] | Partial Wet/Partial Dry | Test fractions of %wet until Ts,2 = Entering Dew Point Temperature
All Wet Case |  |  |  | All Dry Case | 0.00014314 | K/W
X' | 0.14414 | s/kg |  | X | -3.7838e-05 | K/W |  |  | % Wet | Dry Overall Area, Ao (m²) | Wet Overall Area, Ao (m2) | Modified Dry Uao (W/K) | Modified Wet UcAo (W / (J/kg)) | Z | W (K/W) | K1 | K2 | Z' | W' (s/kg) | K3 | K4 | K5 | K6 (kg-K/J) | Tw,2 (°C) | Ta,2 (°C) | Modified dry, air-side resistance (K/W) | Modified Total Dry Resistance (K/W) | Ts,2 (°C) | Ts,2 - Tdp
Y' | -0.10245 | s/kg |  | Y | 0.0001053 | K/W |  |  | 0.05 | 319.4098 | 16.811 | 13977.7623 | 0.61811 | 4.3574 | 0.00058588 | 0.82027 | 0.78317 | 1.0261 | 0.045454 | 0.91722 | 0.082782 | 0.94116 | 2.1731e-05 | 7.6427 | 11.1618 | 5.9576e-05 | 7.1542e-05 | 8.2313 | -8.2089
X'+Y' | 0.041691 | s/kg |  | X+Y |  |  |  |  | 0.1 | 302.5988 | 33.6221 | 13242.0906 | 1.2362 | 4.0326 | 0.00053939 | 0.80478 | 0.78726 | 1.0529 | 0.049315 | 0.84541 | 0.15459 | 0.89012 | 4.0582e-05 | 8.0327 | 11.7789 | 6.2885e-05 | 7.5517e-05 | 8.6593 | -7.7809
Wet air side resistance, Re,w | 5.0204e-06 | K/W |  |  | 5.6597e-05 | K/W |  |  | 0.15 | 285.7877 | 50.4331 | 12506.4189 | 1.8543 | 3.732 | 0.00049636 | 0.78785 | 0.79174 | 1.0804 | 0.053277 | 0.78254 | 0.21746 | 0.84544 | 5.7084e-05 | 8.3974 | 12.3911 | 6.6584e-05 | 7.9959e-05 | 9.0654 | -7.3748
Wet air side resistance, Ra,w | 3.6264e-05 | K/W |  | Ro |  |  |  |  | 0.2 | 268.9767 | 67.2442 | 11770.7472 | 2.4724 | 3.4538 | 0.00045654 | 0.76935 | 0.79663 | 1.1086 | 0.057342 | 0.72706 | 0.27294 | 0.80601 | 7.1648e-05 | 8.7415 | 13.0041 | 7.0746e-05 | 8.4956e-05 | 9.4545 | -6.9857
Total Resistance, wet air side | 1.8508e-05 | K/W |  |  | 6.7965e-05 | K/W |  |  | 0.25 | 252.1656 | 84.0552 | 11035.0755 | 3.0905 | 3.1964 | 0.00041969 | 0.74909 | 0.80198 | 1.1375 | 0.061514 | 0.67776 | 0.32224 | 0.77096 | 8.459e-05 | 9.0687 | 13.6235 | 7.5462e-05 | 9.062e-05 | 9.8306 | -6.6096
|  |  |  | 1/UAo | 14713.434 | W/K |  |  | 0.3 | 235.3546 | 100.8663 | 10299.4038 | 3.7087 | 2.9581 | 0.00038558 | 0.7269 | 0.80785 | 1.1672 | 0.065794 | 0.63367 | 0.36633 | 0.73963 | 9.6164e-05 | 9.3824 | 14.2545 | 8.0853e-05 | 9.7093e-05 | 10.1974 | -6.2428
|  |  |  | UAo |  |  |  |  | 0.35 | 218.5436 | 117.6773 | 9563.7321 | 4.3268 | 2.7376 | 0.00035402 | 0.70255 | 0.81428 | 1.1977 | 0.070186 | 0.59402 | 0.40598 | 0.71144 | 0.00010657 | 9.6858 | 14.9019 | 8.7072e-05 | 0.00010456 | 10.5582 | -5.882
Total Resistance | 2.9876e-05 | K/W |  |  | 4.7084 |  |  |  | 0.4 | 201.7325 | 134.4883 | 8828.0604 | 4.9449 | 2.5335 | 0.00032481 | 0.6758 | 0.82136 | 1.2289 | 0.074692 | 0.55817 | 0.44183 | 0.68597 | 0.00011598 | 9.9814 | 15.5708 | 9.4328e-05 | 0.00011328 | 10.9163 | -5.5239
|  |  |  | Z | 0.00063612 | K/W |  |  | 0.45 | 184.9215 | 151.2994 | 8092.3887 | 5.563 | 2.3447 | 0.00029778 | 0.64637 | 0.82914 | 1.261 | 0.079317 | 0.52563 | 0.47437 | 0.66284 | 0.00012452 | 10.2717 | 16.2659 | 0.0001029 | 0.00012357 | 11.2744 | -5.1658
N | 2.8764 |  |  | W |  |  |  |  | 0.5 | 168.1104 | 168.1104 | 7356.717 | 6.1811 | 2.1699 | 0.00027276 | 0.61394 | 0.83771 | 1.2939 | 0.084062 | 0.49596 | 0.50404 | 0.64175 | 0.00013231 | 10.5592 | 16.9922 | 0.00011319 | 0.00013593 | 11.6353 | -4.8049
[5 empty] | 0.83446 |  |  |  | 0.55 | 151.2994 | 184.9215 | 6621.0453 | 6.7992 | 2.0081 | 0.00024961 | 0.57813 | 0.84718 | 1.3277 | 0.088931 | 0.46881 | 0.53119 | 0.62245 | 0.00013944 | 10.8461 | 17.7547 | 0.00012577 | 0.00015103 | 12.0017 | -4.4385
1/UcAo | 0.080892 | (J/kg) / W |  | K1 | 0.77942 |  |  |  | 0.6 | 134.4883 | 201.7325 | 5885.3736 | 7.4173 | 1.8584 | 0.00022818 | 0.53851 | 0.85765 | 1.3624 | 0.093927 | 0.44387 | 0.55613 | 0.60473 | 0.00014599 | 11.1344 | 18.5587 | 0.00014149 | 0.00016991 | 12.3762 | -4.064
UcAo | 12.3622 | W / (J/kg) |  | K2 |  |  |  |  | 0.65 | 117.6773 | 218.5436 | 5149.7019 | 8.0354 | 1.7199 | 0.00020835 | 0.49459 | 0.86926 | 1.398 | 0.099053 | 0.4209 | 0.5791 | 0.5884 | 0.00015202 | 11.4263 | 19.4097 | 0.00016171 | 0.00019419 | 12.7616 | -3.6786
[5 empty] | 27.2222 | °C |  |  | 0.7 | 100.8663 | 235.3546 | 4414.0302 | 8.6535 | 1.5917 | 0.00019 | 0.44577 | 0.88216 | 1.4344 | 0.10431 | 0.39968 | 0.60032 | 0.57331 | 0.00015759 | 11.7238 | 20.3134 | 0.00018866 | 0.00022655 | 13.1605 | -3.2797
Z' | 1.6743 |  |  | Entering Air Temp, Ta,1 | 7.2222 | °C |  |  | 0.75 | 84.0552 | 252.1656 | 3678.3585 | 9.2716 | 1.4731 | 0.00017301 | 0.39137 | 0.89654 | 1.4719 | 0.10971 | 0.38001 | 0.61999 | 0.55934 | 0.00016275 | 12.029 | 21.276 | 0.00022639 | 0.00027186 | 13.5757 | -2.8645
W' | 0.13889 | s/kg |  | Entering Water Temp, Tw,2 |  |  |  |  | 0.8 | 67.2442 | 268.9767 | 2942.6868 | 9.8898 | 1.3632 | 0.0001573 | 0.33055 | 0.91262 | 1.5103 | 0.11525 | 0.36175 | 0.63825 | 0.54636 | 0.00016754 | 12.344 | 22.3042 | 0.00028298 | 0.00033983 | 14.01 | -2.4302
[5 empty] | 10.533 | °C |  |  | 0.85 | 50.4331 | 285.7877 | 2207.0151 | 10.5079 | 1.2616 | 0.00014275 | 0.26234 | 0.93065 | 1.5497 | 0.12093 | 0.34475 | 0.65525 | 0.53428 | 0.00017201 | 12.6711 | 23.4049 | 0.00037731 | 0.0004531 | 14.4665 | -1.9737
K3 | 0.30018 | Unitless |  | Leaving Air Temp, Ta,2 | 50.9593 | °F |  |  | 0.9 | 33.6221 | 302.5988 | 1471.3434 | 11.126 | 1.1676 | 0.00012929 | 0.18553 | 0.95096 | 1.5902 | 0.12676 | 0.32889 | 0.67111 | 0.523 | 0.00017617 | 13.0125 | 24.5858 | 0.00056597 | 0.00067965 | 14.9483 | -1.4919
K4 | 0.69982 | Unitless |  |  | 11.6339 | °C |  |  | 0.95 | 16.811 | 319.4098 | 735.6717 | 11.7441 | 1.0805 | 0.00011683 | 0.098685 | 0.97391 | 1.6317 | 0.13275 | 0.31407 | 0.68593 | 0.51247 | 0.00018006 | 13.3706 | 25.8553 | 0.0011319 | 0.0013593 | 15.4588 | -0.98136
K5 | 0.5026 | Unitless |  | Leaving Water Temp, Tw,3 | 52.941 | °F |  |  | 1 | 0 | 336.2209 | 0 | 12.3622 | 1 | 0.0001053 | 0 | 1 | 1.6743 | 0.13889 | 0.30018 | 0.69982 | 0.5026 | 0.00018371 | 13.7479 | 27.2222 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
K6 | 0.00018371 | kg-K/J
Rx | 0.61425
1/(Rx+1) | 0.61948
Rx/b | 0.00022686 | kg-K/J
Leaving Air Enthalpy ha,3 | 51194.4683 | J/kg
Leaving Water Temperature, Tw,2 | 13.7479 | °C
| 56.7462 | °F
Ent. Air side Coil Surface Temp Ts,2 | 16.257 | °C
| 61.2625 | °F
Leav. Air Side Coil Surface Temp, Ts,3 | 8.8682 | °C
| 47.9627 | °F
N | 2.8764
Leaving Air Temperature, Ta,3 | 9.4859 | °C
| 49.0746 | °F
Q total | 165.1881 | kW
| 563645.1854 | BTU/hr
Q sensible | 123.9093 | kW
| 422796.1107 | BTU/hr
Is coil completely Wet? | YES
Is coil completely Dry? | NO
Note on H3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From EnergyPlus engineering reference, pg. 815, assumes some water vapor
Note on H4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From EnergyPlus engineering reference, pg. 815
Note on D74: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I actually think the equation as written is incorrect. It only subtracts the tube area from 1 fin side, instead of all fin sides

## Saturated Air Enthalpy
[7 empty] | Average Temp | 14
Temperature (C) | Temperature (F) | Saturated Partial Pressure (psia) | Saturated Air Enthalpy (BTU/lb) | Saturated Air Enthalpy (J/kg) |  |  | Average Enthalpy | 57834.0705
8 | 46.4 | 0.1556 | 18.3348 | 42646.7028 | 91124.2064 | 36 | a | 19927.6793 | J/kg
9 | 48.2 | 0.16652 | 19.2833 | 44853.002 | 64905.3426 | 25 | b | 2707.5994 | J/kg-K
10 | 50 | 0.17811 | 20.2648 | 47136.0217 | 42792.195 | 16
11 | 51.8 | 0.1904 | 21.2812 | 49500.0945 | 25001.9281 | 9
12 | 53.6 | 0.20343 | 22.3344 | 51949.7732 | 11768.5946 | 4
13 | 55.4 | 0.21724 | 23.4264 | 54489.843 | 3344.2275 | 1
14 | 57.2 | 0.23187 | 24.5595 | 57125.333 | 0 | 0
15 | 59 | 0.24735 | 25.7358 | 59861.5289 | 2027.4584 | 1
16 | 60.8 | 0.26374 | 26.9579 | 62703.9869 | 9739.8329 | 4
17 | 62.6 | 0.28108 | 28.2281 | 65658.548 | 23473.4325 | 9
18 | 64.4 | 0.2994 | 29.5492 | 68731.3536 | 43589.1323 | 16
19 | 66.2 | 0.31876 | 30.9238 | 71928.8621 | 70473.9579 | 25
20 | 68 | 0.33921 | 32.3551 | 75257.8668 | 104542.7778 | 36