## Internal h
Pr | 8 | Prantl number water ~ 60°F
mu | 0.00108 | N s /m2
specific volume water | 0.001 | m3/kg
kinematic viscosity | 1.08e-06 | m2/s
Outer Diameter Coil Tube | 0.625 | in
Wall thickness | 0.02 | in
Inner Diameter Coil Tube | 0.585 | in
| 0.014859 | m
Thermal conductivity water | 0.59 | W/m-K
Velocity (fps) | Velocity (m/s) | Re | NuD | h (W/m2-K) | dh/dV (W/m2-K) / (m/s)
1 | 0.3048 | 4193.54 | 41.7858 | 1659.17 | 4354.777
1.25 | 0.381 | 5241.925 | 49.9524 | 1983.4392 | 4164.7018
1.5 | 0.4572 | 6290.31 | 57.7965 | 2294.9007 | 4015.5743
1.75 | 0.5334 | 7338.695 | 65.3821 | 2596.0995 | 3893.6625
2 | 0.6096 | 8387.08 | 72.7533 | 2888.7828 | 3791.0535
2.25 | 0.6858 | 9435.465 | 79.9419 | 3174.2191 | 3702.7928
2.5 | 0.762 | 10483.85 | 86.9722 | 3453.3683 | 3625.5835
2.75 | 0.8382 | 11532.235 | 93.863 | 3726.9799 | 3557.1271
3 | 0.9144 | 12580.62 | 100.6295 | 3995.6542 | 3495.7605
3.25 | 0.9906 | 13629.005 | 107.284 | 4259.8821 | 3440.244
3.5 | 1.0668 | 14677.39 | 113.8369 | 4520.0717 | 3389.6301
3.75 | 1.143 | 15725.775 | 120.2966 | 4776.5674 | 3343.1792
4 | 1.2192 | 16774.16 | 126.6708 | 5029.663 | 3300.3038
4.25 | 1.2954 | 17822.545 | 132.9657 | 5279.6123 | 3260.5295
4.5 | 1.3716 | 18870.93 | 139.1869 | 5526.6365 | 3223.4684
4.75 | 1.4478 | 19919.315 | 145.3394 | 5770.9296 | 3188.7994
5 | 1.524 | 20967.7 | 151.4274 | 6012.6634 | 3156.2538
5.25 | 1.6002 | 22016.085 | 157.4548 | 6251.9909 | 3125.6047
5.5 | 1.6764 | 23064.47 | 163.425 | 6489.0488 | 3096.659
5.75 | 1.7526 | 24112.855 | 169.3412 | 6723.9607 | 3069.2506
6 | 1.8288 | 25161.24 | 175.2062 | 6956.838 | 3043.2362
6.25 | 1.905 | 26209.625 | 181.0225 | 7187.7821 | 3018.4912
6.5 | 1.9812 | 27258.01 | 186.7924 | 7416.8855 | 2994.9063
6.75 | 2.0574 | 28306.395 | 192.5181 | 7644.2329 | 2972.3857
7 | 2.1336 | 29354.78 | 198.2015 | 7869.902 | 2950.8444
7.25 | 2.2098 | 30403.165 | 203.8444 | 8093.9645 | 2930.2071
7.5 | 2.286 | 31451.55 | 209.4486 | 8316.4868 | 2910.4066
7.75 | 2.3622 | 32499.935 | 215.0155 | 8537.5302 | 2891.3827
8 | 2.4384 | 33548.32 | 220.5466 | 8757.1519 | 2873.0813
8.25 | 2.5146 | 34596.705 | 226.0433 | 8975.4049 | 2855.4537
8.5 | 2.5908 | 35645.09 | 231.5067 | 9192.339 | 2838.4558
8.75 | 2.667 | 36693.475 | 236.9381 | 9408.0005 | 2822.0474
9 | 2.7432 | 37741.86 | 242.3385 | 9622.4331 | 2806.1922
9.25 | 2.8194 | 38790.245 | 247.709 | 9835.6774 | 2790.8569
9.5 | 2.8956 | 39838.63 | 253.0506 | 10047.7721 | 2776.0111
9.75 | 2.9718 | 40887.015 | 258.3641 | 10258.7533 | 2761.6268
10 | 3.048 | 41935.4 | 263.6504 | 10468.6551 | 2747.6785
10.25 | 3.1242 | 42983.785 | 268.9104 | 10677.5099 | 2734.1425
10.5 | 3.2004 | 44032.17 | 274.1447 | 10885.3483 | 2720.997
10.75 | 3.2766 | 45080.555 | 279.3542 | 11092.1993 | 2708.2218
11 | 3.3528 | 46128.94 | 284.5395 | 11298.0903 | 2695.7982
11.25 | 3.429 | 47177.325 | 289.7013 | 11503.0474 | 2683.7089
11.5 | 3.5052 | 48225.71 | 294.8402 | 11707.0956 | 2671.9378
11.75 | 3.5814 | 49274.095 | 299.9568 | 11910.2584 | 2660.4699
12 | 3.6576 | 50322.48 | 305.0517 | 12112.5585 | 2649.291
12.25 | 3.7338 | 51370.865 | 310.1254 | 12314.0174 | 2638.3882
12.5 | 3.81 | 52419.25 | 315.1784 | 12514.6556 | 2627.7492
Note on C24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Coil manufacturers recommend speeds > 2.5 because this is the transition to turbulent flow, as evidenced by this Reynolds number calculation

## Sheet2
Example Coil
1st floor 1P-6
Air flow | 11700 | CFM
Entering Air Temp | 76 | °F
Leaving Air Temp | 56 | °F
Entering Air Wetbulb | 63.5 | °F
Entering Air Specific Volume | 13.7135 | ft³/lb
Air specific volume | 13.5 | ft³/lb
Specific Heat Air | 0.24 | BTU/lb-°F
Mass flow rate | 51190.4172 | lb/hr
Water flow | 49 | gal/min
Specific Heat Water | 1 | BTU/lb-°F
Water density | 62.4 | lb/ft³
Water density | 8.3417 | lb/gal
Water entering temp | 45 | °F
Water leaving temp | 57 | °F
Water mass flow rate | 24524.4999 | lb/hr
Air energy | 245714.0025 | BTU/hr
Water energy | 294293.9992
Air Capacity | 12285.7001 | BTU/°F
Water capacity | 24524.4999 | BTU/°F

## Full Coil Model
Entering Air Dry Bulb | 84.7 | °F
| 29.2778 | °C |  |  | Property | Unit | Air | Water |  |  | Rows | 1/2" tube | 5/8" tube
Entering Air Wet Bulb | 68.2 | °F |  |  | Pr |  | 0.733 | 8 |  |  | 1 | 5.5 | 5.5
| 20.1111 | °C |  |  | mu | N s /m² | 1.846e-05 | 0.00108 |  |  | 2 | 6.5 | 6.5
Entering Air w* | 0.014799 |  |  |  | specific volume | m³/kg |  | 0.001 |  |  | 3 | 6.5 | 6.5
Entering Air w | 0.010969 |  |  |  | kinematic viscosity | m²/s |  | 1.08e-06 |  |  | 4 | 6.5 | 7.5
Entering Air Partial Pressure | 0.25471 | psia |  |  | Thermal Conductivity | W/m-K |  | 0.59 |  |  | 5 | 7.5 | 8.75
Entering Air Enthalpy | 32.3791 | BTU/lb |  |  | Specific Heat | J/kg-K | 1007 | 4189 |  |  | 6 | 8.5 | 10
| 75313.7373 | J/kg | [8 empty] | 8 | 10.5 | 12.5
Entering Air Dew Point Temperature | 59.8741 | °F | [8 empty] | 10 | 13 | 15
| 15.4856 | °C | [8 empty] | 12 | 15 | 17.5
Entering Air Specific Volume | 13.9656 | ft³/lb
| 0.87184 | m³/kg
Entering Water Temperature | 47.3 | °F
| 8.5 | °C
Sat. Partial pressure @ Water Ent. Temp | 0.16098 | psia
Sat. Air Enthalpy @ Water Ent. Temp | 18.805 | BTU/lb
| 43740.5247 | J/kg
Water flow, GPM | 35.3125 | GPM
| 0.0022279 | m³/s
Mass flow rate, water | 2.2279 | kg/s
Air Volumetric Flow Rate | 3276 | CFM
| 1.5461 | m³/s
Air density | 1.147 | kg/m³
Mass flow rate, air | 14074.5753 | lbm/hr
| 1.7734 | kg/s
Fin thickness | 0.0065 | in
| 0.0001651 | m
Fins per inch | 11.8 | fins/in
Fin spacing | 0.078246 | in
| 0.0019874 | m
Tube thickness | 0.025 | in
| 0.000635 | m
Tube Material | Copper
Copper thermal conductivity | 385 | W/m-K
Aluminum thermal conductivity | 237 | W/m-K
Number of Rows | 8 | Count
Number of Tubes/Row, # of circuits | 16 | Count
Number of Tubes | 128 | Count
Number of Passes | 8
Tube OD | 0.625 | in
| 0.015875 | m
| 0.052083 | ft
Tube Outer Radius | 0.3125 | in
| 0.0079375 | m
Tube Outer Area | 0.00019793 | m²
Tube ID | 0.575 | in
| 0.014605 | m
Tube Inner Area | 0.00016753 | m²
Water Velocity | 0.83115 | m/s
| 2.7269 | fps
Water Re | 11239.7116
Water Nu [1] | 91.9534 |  | Using 0.023 * Re^0.8 Pr^0.4 formulation
Water heat transfer coefficient, hi, fi, [1] | 3714.6544 | W/m²-K
Mean water temperature for [2] | 9.43 | °C
Water heat transfer coefficient, hi, fi [2] | 3265.075 | W/m²-K | Using 1429[1+0.0146 Tw,m] V^0.8 Di^-0.2
Correlation Used | 1
Used Water heat transfer coefficient, hi, fi | 3714.6544 | W/m²-K
Internal Thermal Resistance, Ri | 7.5193e-05 | K/W
Roughness, E | 0.0015 | mm | https://docs.bentley.com/LiveContent/web/Bentley%20HAMMER%20SS6-v1/en/GUID-3EB84F7E-B48C-4063-99B9-D3EDCFD864C8.html
E/D | 0.0001027
1/sqrt(f) | 5.7704
f | 0.030033 |  | Haaland equation: https://en.wikipedia.org/wiki/Darcy_friction_factor_formulae
Total pipe length | 4.8768 | m
Pipe DP | 0.35321 | m H2O
| 1.1588 | ft H2O
Distance between tube rows | 1.29 | in
| 0.032766 | m |  | 104.0457
Percent fins | 0.0767
Percent non-fin | 0.9233
Ap | 3.593 | m² | Equation 77, Area of exposed tube | Elmahdy dimensions pg. 68(80) in dissertation
| 38.6751 | ft2 |  | 38.9
As | 104.0457 | m² | Equation 78, Fin area
| 1119.9383 | ft2 |  | 827 | 1273.8546
Ao | 107.6387 | m² | Equation 79, Total air side heat transfer area
865.9
Am,f | 0.20015 | m² | Min cross-sectional area: This accounts for the cross-sectional area of the tubes
| 2.1544 | ft2
Ai,w | 3.5802 | m²
Coil Height | 24 | in
| 0.6096 | m
| 2 | ft
Coil Width | 24 | in
| 0.6096 | m
| 2 | ft
Coil Depth | 13.5 | in
| 0.3429 | m
| 1.125 | ft
Face Area | 576 | in²
| 4 | ft2
| 0.37161 | m2
Min flow area/Face Area, Ar | 0.53859
Equivalent Fin Diameter | 1.7952 | in
| 0.045599 | m
Equivalent Fin Radius | 0.89762 | in
| 0.0228 | m
Fin Length | 0.58512 | in
| 0.014862 | m
Total # of Fins | 283.2
Hydraulic Diameter | 0.0025504 | m | From Dissertation: |  | 0.0913
| 0.10041 | in
| 0.0083675 | ft | 9.1926 | ft
Air Velocity through minimum area | 7.7248 | m/s
| 1520.6325 | ft/min
Air Face Velocity | 819 | ft/min
Fin thickness/Hydraulic Diameter (Ft/Dh) | 0.064735
Fin thickness/Fin length (Ft/Fh) | 0.011109
Fin spacing/Fin length (Fs/Fh) | 0.13373
Fin Diameter, eq/Distance between tube rows (Fd/Sl) | 1.3917
Fin thickness/Fin spacing (Ft/Fs) | 0.083072
C1 | 0.10072
C2 | -0.37622
Reynolds Number | 1224.1251
Stanton Number | 0.0085377
Dry heat transfer coefficient, ho, fo | 76.1762 | W/m²-K
Adjusted wet heat transfer coefficient, ho,w fo,w | 91.0151 | W/m²-K
[9 empty] | Resistances | K/W * 10^6
[9 empty] | Air side, dry | 175.8114
[9 empty] | Air side, wet | 155.3034
Wall Resistance, Rm | 4.6069e-07 | K/W | [6 empty] | Water side | 75.1926
[9 empty] | Fouling | 13.9657
Wall Resistance calc 2, Rm | 4.4175e-07 | K/W | 1.0429 | [5 empty] | Tube wall | 0.44175
Fouling Resistance
Fouling Factor | 5e-05 | m2-K/W
Rf | 1.3966e-05 | K/W
Dry
m (Dry) | 62.3989 | 1/m | See Incropera pg. 151
C2 (circular fin) | 0.55692
m r1 | 0.49529
m r2 | 1.4227
Fin Numerator | 1.4416
Fin Denominator | 1.1753
Dry Fin efficiency | 0.68311
Dry Overall efficiency | 0.69369
Ra,dry | 0.00017581 | K/W
Wet
m (Wet) | 68.2062 | 1/m
C2 (circular fin) | 0.50951
m r1 | 0.54139
m r2 | 1.5551
Fin Numerator | 1.4784
Fin Denominator | 1.1671
Wet Fin Efficiency | 0.64542
Wet Overall Efficiency | 0.65726
Ra, wet | 0.0001553 | K/W
All Cases
Sum of Constant Resistances (Rm + Ri + Rf) | 8.96e-05 | K/W
a | 19927.6793 | J/kg
b | 2707.5994 | J/kg-K
All Wet Case |  |  |  | All Dry Case | [5 empty] | Partial Wet/Partial Dry | Test fractions of %wet until Ts,2 = Entering Dew Point Temperature
X' | 0.5639 | s/kg |  | X | 0.00055998 | K/W
Y' | -0.29012 | s/kg |  | Y | -0.00010715 | K/W |  |  |  | % Wet | Dry Overall Area, Ao (m²) | Wet Overall Area, Ao (m2) | Modified Dry UAo (W/K) | Modified Wet UcAo (W / (J/kg)) | Z | W (K/W) | K1 | K2 | Z' | W' (s/kg) | K3 | K4 | K5 | K6 (kg-K/J) | Tw,2 (°C) | Ta,2 (°C) | Ta,2 (°F) | Modified dry, air-side resistance (K/W) | Modified Total Dry Resistance (K/W) | Ts,2 (°C) | Ts,2 - Tdp | abs(Ts,2 - Tdp) | Tw3 (°C) | Tw3 (°F) | N | ha,2 (BTU/lb) | ha,2 (J/kg) | ha,3 | Ts,3 (°C) | Ta,3 (°C) | Ta,3 (°F) | Air DT (°F) | Water DT (°F) | Q total (BTU/hr) | Q sensible (BTU/hr) | Q total (kW) | Q sensible (kW) | SHR
X'+Y' | 0.27378 | s/kg |  | X+Y | 0.00045283 | K/W |  |  |  | 0.05 | 102.2568 | 5.3819 | 3579.3479 | 0.12532 | 5.0573 | 0.0027248 | 0.83381 | 0.84045 | 1.0349 | 0.29346 | 0.93293 | 0.06707 | 0.96549 | 1.2745e-05 | 8.6923 | 12.1133 | 53.804 | 0.00018506 | 0.00027938 | 9.8472 | -5.6384 | 5.6384 | 11.9767 | 53.558 | 0.18029 | 24.8136 | 57716.3186 | 56778.9629 | 11.6073 | 13.4995 | 56.2992 | 28.4008 | 6.258 | 112153.5137 | 96142.0736 | 32.869 | 28.1765 | 0.85724
Wet air side resistance, Re,w | 1.9797e-05 | K/W | [7 empty] | 0.1 | 96.8748 | 10.7639 | 3390.9612 | 0.25063 | 4.6437 | 0.0024932 | 0.81838 | 0.8434 | 1.071 | 0.31383 | 0.87238 | 0.12762 | 0.93434 | 2.4251e-05 | 8.8773 | 12.5825 | 54.6485 | 0.00019535 | 0.0002949 | 10.1281 | -5.3575 | 5.3575 | 12.072 | 53.7295 | 0.36057 | 25.0203 | 58197.3322 | 56352.3187 | 11.5114 | 13.2228 | 55.801 | 28.899 | 6.4295 | 114735.1288 | 97828.3561 | 33.6255 | 28.6707 | 0.85265
Wet air side resistance, Ra,w | 0.00010207 | K/W |  | Ro | 0.00017581 | K/W |  |  |  | 0.15 | 91.4929 | 16.1458 | 3202.5745 | 0.37595 | 4.264 | 0.0022806 | 0.80144 | 0.84664 | 1.1084 | 0.33491 | 0.81747 | 0.18253 | 0.90609 | 3.4685e-05 | 9.0568 | 13.0717 | 55.5291 | 0.00020684 | 0.00031225 | 10.4122 | -5.0734 | 5.0734 | 12.1578 | 53.884 | 0.54086 | 25.236 | 58698.9306 | 55968.5318 | 11.4253 | 12.9738 | 55.3528 | 29.3472 | 6.584 | 117057.4148 | 99345.6573 | 34.3061 | 29.1153 | 0.84869
Total Resistance, wet air side | 5.776e-05 | K/W | [7 empty] | 0.2 | 86.111 | 21.5277 | 3014.1877 | 0.50126 | 3.9154 | 0.0020854 | 0.78285 | 0.8502 | 1.1471 | 0.35672 | 0.76747 | 0.23253 | 0.88037 | 4.4184e-05 | 9.2321 | 13.5849 | 56.4528 | 0.00021976 | 0.00033176 | 10.7015 | -4.7841 | 4.7841 | 12.2349 | 54.0228 | 0.72114 | 25.4622 | 59225.0355 | 55624.4822 | 11.348 | 12.7499 | 54.9498 | 29.7502 | 6.7228 | 119139.2515 | 100710.0483 | 34.9163 | 29.5152 | 0.84531
|  |  |  | 1/UAo | 0.00026541 | K/W |  |  |  | 0.25 | 80.729 | 26.9097 | 2825.801 | 0.62658 | 3.5952 | 0.0019061 | 0.76243 | 0.85411 | 1.1871 | 0.3793 | 0.72179 | 0.27821 | 0.85686 | 5.2865e-05 | 9.4047 | 14.1259 | 57.4267 | 0.00023442 | 0.00035388 | 10.9985 | -4.4871 | 4.4871 | 12.304 | 54.1472 | 0.90143 | 25.7007 | 59779.7139 | 55317.4667 | 11.2791 | 12.5487 | 54.5877 | 30.1123 | 6.8472 | 120996.9951 | 101935.6347 | 35.4607 | 29.8744 | 0.84246
|  |  |  | UAo | 3767.7347 | W/K |  |  |  | 0.3 | 75.3471 | 32.2916 | 2637.4143 | 0.7519 | 3.3012 | 0.0017415 | 0.73997 | 0.85841 | 1.2286 | 0.40267 | 0.67991 | 0.32009 | 0.83531 | 6.0824e-05 | 9.576 | 14.699 | 58.4582 | 0.00025116 | 0.00037916 | 11.3055 | -4.1801 | 4.1801 | 12.3657 | 54.2582 | 1.0817 | 25.9532 | 60367.2247 | 55045.1471 | 11.2179 | 12.3683 | 54.263 | 30.437 | 6.9582 | 122644.7952 | 103034.8171 | 35.9436 | 30.1965 | 0.84011
Total Resistance | 0.00014736 | K/W | [7 empty] | 0.35 | 69.9652 | 37.6735 | 2449.0275 | 0.87721 | 3.0313 | 0.0015903 | 0.71526 | 0.86314 | 1.2715 | 0.42685 | 0.64139 | 0.35861 | 0.8155 | 6.8143e-05 | 9.7473 | 15.3085 | 59.5552 | 0.00027048 | 0.00040833 | 11.6247 | -3.8609 | 3.8609 | 12.4203 | 54.3566 | 1.262 | 26.2219 | 60992.0654 | 54805.5054 | 11.1641 | 12.2069 | 53.9724 | 30.7276 | 7.0566 | 124094.8618 | 104018.5111 | 36.3686 | 30.4848 | 0.83822
|  |  |  | Z | 5.5076 |  |  |  |  | 0.4 | 64.5832 | 43.0555 | 2260.6408 | 1.0025 | 2.7834 | 0.0014515 | 0.68803 | 0.86835 | 1.3158 | 0.45187 | 0.60587 | 0.39413 | 0.79722 | 7.4892e-05 | 9.9199 | 15.959 | 60.7262 | 0.00029302 | 0.00044235 | 11.9586 | -3.527 | 3.527 | 12.4685 | 54.4432 | 1.4423 | 26.5086 | 61659.019 | 54596.807 | 11.1172 | 12.0628 | 53.7131 | 30.9869 | 7.1432 | 125357.6913 | 104896.3325 | 36.7387 | 30.7421 | 0.83678
|  |  |  | W | 0.002977 | K/W |  |  |  | 0.45 | 59.2013 | 48.4374 | 2072.2541 | 1.1278 | 2.5558 | 0.0013241 | 0.658 | 0.87409 | 1.3618 | 0.47777 | 0.57303 | 0.42697 | 0.78032 | 8.1133e-05 | 10.0952 | 16.6556 | 61.9801 | 0.00031966 | 0.00048257 | 12.3099 | -3.1757 | 3.1757 | 12.5104 | 54.5187 | 1.6226 | 26.8157 | 62373.2022 | 54417.5691 | 11.077 | 11.9348 | 53.4826 | 31.2174 | 7.2187 | 126442.2558 | 105676.7546 | 37.0566 | 30.9708 | 0.83577
[10 empty] | 0.5 | 53.8194 | 53.8194 | 1883.8673 | 1.2532 | 2.3468 | 0.001207 | 0.62484 | 0.88044 | 1.4093 | 0.50457 | 0.54259 | 0.45741 | 0.76466 | 8.6917e-05 | 10.2743 | 17.4037 | 63.3266 | 0.00035162 | 0.00053082 | 12.6811 | -2.8045 | 2.8045 | 12.5464 | 54.5836 | 1.8029 | 27.1454 | 63140.115 | 54266.5345 | 11.043 | 11.8215 | 53.2786 | 31.4214 | 7.2836 | 127356.1633 | 106367.2421 | 37.3244 | 31.1732 | 0.8352
1/UcAo | 0.39899 | (J/kg) / W |  | K1 | 0.84789 |  |  |  |  | 0.55 | 48.4374 | 59.2013 | 1695.4806 | 1.3785 | 2.1549 | 0.0010996 | 0.58818 | 0.88745 | 1.4585 | 0.53231 | 0.51432 | 0.48568 | 0.75012 | 9.2289e-05 | 10.4589 | 18.2089 | 64.7761 | 0.00039069 | 0.0005898 | 13.0752 | -2.4104 | 2.4104 | 12.5769 | 54.6384 | 1.9831 | 27.5003 | 63965.6944 | 54142.649 | 11.0152 | 11.7218 | 53.0993 | 31.6007 | 7.3384 | 128105.7913 | 106974.3655 | 37.5441 | 31.3511 | 0.83505
UcAo | 2.5063 | W / (J/kg) |  | K2 | 0.83776 |  |  |  |  | 0.6 | 43.0555 | 64.5832 | 1507.0939 | 1.5038 | 1.9787 | 0.0010009 | 0.54758 | 0.89522 | 1.5094 | 0.56102 | 0.488 | 0.512 | 0.73658 | 9.729e-05 | 10.6501 | 19.0777 | 66.3398 | 0.00043953 | 0.00066353 | 13.4952 | -1.9904 | 1.9904 | 12.6019 | 54.6834 | 2.1634 | 27.8832 | 64856.3704 | 54045.0437 | 10.9933 | 11.6349 | 52.9428 | 31.7572 | 7.3834 | 128696.3988 | 107503.8987 | 37.7172 | 31.5063 | 0.83533
[10 empty] | 0.65 | 37.6735 | 69.9652 | 1318.7071 | 1.6291 | 1.8169 | 0.00091029 | 0.50255 | 0.90384 | 1.5621 | 0.59072 | 0.46346 | 0.53654 | 0.72395 | 0.00010195 | 10.8496 | 20.0168 | 68.0302 | 0.00050232 | 0.00075832 | 13.9443 | -1.5413 | 1.5413 | 12.6217 | 54.719 | 2.3437 | 28.2971 | 65819.1275 | 53973.0189 | 10.9771 | 11.5599 | 52.8078 | 31.8922 | 7.419 | 129132.2195 | 107960.9034 | 37.8449 | 31.6402 | 0.83605
Z' | 1.9861 |  |  | Entering Air Temp, Ta,1 | 29.2778 | °C |  |  |  | 0.7 | 32.2916 | 75.3471 | 1130.3204 | 1.7544 | 1.6684 | 0.00082709 | 0.45251 | 0.91341 | 1.6166 | 0.62147 | 0.44053 | 0.55947 | 0.71215 | 0.00010631 | 11.0588 | 21.0336 | 69.8604 | 0.00058604 | 0.0008847 | 14.4262 | -1.0594 | 1.0594 | 12.6364 | 54.7455 | 2.524 | 28.7453 | 66861.5712 | 53926.0317 | 10.9666 | 11.4961 | 52.693 | 32.007 | 7.4455 | 129416.5382 | 108349.8004 | 37.9282 | 31.7542 | 0.83722
W' | 0.82983 | s/kg |  | Entering Water Temp, Tw,2 | 8.5 | °C |  |  |  | 0.75 | 26.9097 | 80.729 | 941.9337 | 1.8797 | 1.5319 | 0.0007507 | 0.39679 | 0.92407 | 1.673 | 0.65329 | 0.41907 | 0.58093 | 0.70112 | 0.00011039 | 11.2795 | 22.1362 | 71.8451 | 0.00070325 | 0.0010616 | 14.9446 | -0.54099 | 0.54099 | 12.6461 | 54.7629 | 2.7043 | 29.2313 | 67992.0005 | 53903.6857 | 10.9616 | 11.4428 | 52.5971 | 32.1029 | 7.4629 | 129551.7535 | 108674.4319 | 37.9679 | 31.8493 | 0.83885
[10 empty] | 0.8 | 21.5277 | 86.111 | 753.5469 | 2.0051 | 1.4067 | 0.00068056 | 0.33462 | 0.93597 | 1.7314 | 0.68621 | 0.39896 | 0.60104 | 0.69077 | 0.00011421 | 11.5135 | 23.3335 | 74.0002 | 0.00087906 | 0.0013271 | 15.5038 | 0.018151 | 0.018151 | 12.6509 | 54.7716 | 2.8846 | 29.759 | 69219.4876 | 53905.7227 | 10.962 | 11.3995 | 52.5192 | 32.1808 | 7.4716 | 129539.4272 | 108938.1144 | 37.9643 | 31.9266 | 0.84096
K3 | 0.32992 | Unitless |  | Leaving Air Temp, Ta,2 | 11.6605 | °C |  |  |  | 0.85 | 16.1458 | 91.4929 | 565.1602 | 2.1304 | 1.2916 | 0.00061615 | 0.26506 | 0.94928 | 1.7918 | 0.72029 | 0.38009 | 0.61991 | 0.68106 | 0.0001178 | 11.7625 | 24.6351 | 76.3432 | 0.0011721 | 0.0017694 | 16.1081 | 0.62254 | 0.62254 | 12.6509 | 54.7715 | 3.0649 | 30.3327 | 70553.9665 | 53932.0167 | 10.9679 | 11.3658 | 52.4584 | 32.2416 | 7.4715 | 129380.3231 | 109143.684 | 37.9176 | 31.9869 | 0.84359
K4 | 0.67008 | Unitless |  |  | 52.9889 | °F |  |  |  | 0.9 | 10.7639 | 96.8748 | 376.7735 | 2.2557 | 1.186 | 0.000557 | 0.18703 | 0.96421 | 1.8544 | 0.75556 | 0.36235 | 0.63765 | 0.67193 | 0.00012117 | 12.0287 | 26.0517 | 78.8931 | 0.0017581 | 0.0026541 | 16.7627 | 1.2771 | 1.2771 | 12.646 | 54.7628 | 3.2451 | 30.9571 | 72006.3298 | 53982.5685 | 10.9793 | 11.3412 | 52.4142 | 32.2858 | 7.4628 | 129074.435 | 109293.5351 | 37.828 | 32.0308 | 0.84675
K5 | 0.65524 | Unitless |  | Leaving Water Temp, Tw,3 | 11.8711 | °C |  |  |  | 0.95 | 5.3819 | 102.2568 | 188.3867 | 2.381 | 1.0891 | 0.00050269 | 0.099199 | 0.98102 | 1.9191 | 0.79206 | 0.34565 | 0.65435 | 0.66334 | 0.00012434 | 12.3143 | 27.595 | 81.671 | 0.0035162 | 0.0053082 | 17.4729 | 1.9873 | 1.9873 | 12.6363 | 54.7454 | 3.4254 | 31.6374 | 73588.5375 | 54057.5034 | 10.9961 | 11.3254 | 52.3858 | 32.3142 | 7.4454 | 128621.0058 | 109389.6532 | 37.6951 | 32.0589 | 0.85048
K6 | 0.00012733 | kg-K/J |  |  | 53.3679 | °F |  |  |  | 1 | 0 | 107.6387 | 0 | 2.5063 | 1 | 0.00045283 | 0 | 1 | 1.9861 | 0.82983 | 0.32992 | 0.67008 | 0.65524 | 0.00012733 | 12.6218 | 29.2778 | 84.7 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 12.6218 | 54.7193 | 3.6057 | 32.3791 | 75313.7373 | 54157.0688 | 11.0185 | #DIV/0! | #DIV/0! | #DIV/0! | 7.4193 | 128018.5375 | #DIV/0! | 37.5185 | #DIV/0! | #DIV/0!
Rx | 1.5513 |  |  | Air Delta T | 17.6173 | °C
1/(Rx+1) | 0.39196 |  |  |  | 31.7111 | °F
Rx/b | 0.00057293 | kg-K/J
|  |  |  | Water Delta T | 3.3711 | °C
Leaving Air Enthalpy ha,3 | 54157.0688 | J/kg |  |  | 6.0679 | °F
Leaving Water Temperature, Tw,2 | 12.6218 | °C
| 54.7193 | °F |  | Mean Water Temp | 10.1855 | °C
[5 empty] | 50.334 | °F
Ent. Air side Coil Surface Temp Ts,2 | 17.3851 | °C
| 63.2933 | °F |  | Q total/sensible | 107136.5654 | BTU/hr
Leav. Air Side Coil Surface Temp, Ts,3 | 11.0185 | °C
| 51.8332 | °F
N | 3.6057
Leaving Air Temperature, Ta,3 | 11.3416 | °C
| 52.4148 | °F
Air DT | 17.9362 | °C
| 32.2852 | °F
Water DT | 4.1218 | °C
| 7.4193 | °F
Q total | 37.5185 | kW
| 128018.5375 | BTU/hr
Q sensible | 32.0301 | kW
| 109291.3491 | BTU/hr
Is coil completely Wet? | NO
Is coil completely Dry? | NO
Note on H3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From EnergyPlus engineering reference, pg. 815, assumes some water vapor
Note on H4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: From EnergyPlus engineering reference, pg. 815
Note on D87: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I actually think the equation as written is incorrect. It only subtracts the tube area from 1 fin side, instead of all fin sides

## Elmahdy Data, 1977
Experimental/Analytical Data from "A Simple Model for Cooling and Dehumidifying Coils for Use in Calculating Energy Requirements for Buildings, 1977
Table 1 | 4 row coil |  |  |  | Delta Tdb |  | Delta WT |  | Qtotal |  | Qsensible
Test | Air Face Velocity (fpm) | Tdb (F) | Twb (F) | Tw (F) | Expt. | Anal. | Expt. | Anal. | Expt. | Anal. | Expt. | Anal. | Condition | GPM | CFM
1 | 312 | 96.1 | 66.9 | 47.1 | 40.6 | 39.8 | 2.8 | 2.8 | 52.9 | 51.8 | 52.9 | 51.8 | Dry | 37.7857 | 1248
2 | 177 | 81.2 | 60.9 | 47.2 | 30.4 | 29.6 | 2.2 | 2.2 | 23.2 | 22.6 | 23.2 | 22.6 | Dry | 21.0909 | 708
3 | 482 | 77.6 | 60.2 | 47.2 | 22.1 | 21.7 | 2.4 | 2.4 | 46 | 45.1 | 46 | 45.1 | Dry | 38.3333 | 1928
4 | 605 | 71.5 | 57.6 | 47.2 | 16.3 | 15.9 | 2.2 | 2.2 | 43 | 42.1 | 43 | 42.1 | Dry | 39.0909 | 2420
5 | 367 | 95.9 | 77.9 | 47.3 | 31 | 30.5 | 7.7 | 7.8 | 78.7 | 79 | 48.1 | 46.8 | Wet | 20.4416 | 1468
6 | 544 | 85.9 | 73.6 | 47.2 | 20.4 | 20 | 7.4 | 7.5 | 77.7 | 77.3 | 47.5 | 46.2 | Wet | 21 | 2176
7 | 667 | 76.6 | 69 | 47.2 | 13.1 | 13.6 | 6.6 | 6.5 | 68.1 | 67.3 | 38 | 39.2 | Wet | 20.6364 | 2668
8 | 818 | 88.2 | 75 | 47.2 | 18.3 | 17.8 | 9 | 9.1 | 93.6 | 94.1 | 64.3 | 61.7 | Wet | 20.8 | 3272
9 | 857 | 96.9 | 79.7 | 47.2 | 23.2 | 21 | 10.9 | 11.1 | 114.3 | 115.3 | 84.2 | 75.1 | Dry-Wet | 20.9725 | 3428
10 | 736 | 74 | 67.5 | 47.2 | 11 | 11.6 | 6.4 | 6.3 | 62.9 | 62.4 | 35.1 | 36.9 | Wet | 19.6562 | 2944
11 | 603 | 86.8 | 74.4 | 47.3 | 19.8 | 19.2 | 7.9 | 8 | 82.4 | 82.8 | 51.3 | 49.2 | Wet | 20.8608 | 2412
12 | 584 | 75.4 | 68.9 | 47.2 | 13.1 | 13.4 | 6.3 | 6.3 | 63 | 63.1 | 33.3 | 33.9 | Wet | 20 | 2336
Table 2 | 8 row coil |  |  |  | Delta Tdb |  | Delta WT |  | Qtotal |  | Qsensible |  |  |  |  | Delta Tdb | Delta WT | Qtotal | Qsensible
Test | Air Face Velocity (fpm) | Tdb (F) | Twb (F) | Tw (F) | Expt. | Anal. | Expt. | Anal. | Expt. | Anal. | Expt. | Anal. | Condition | GPM | CFM
1 | 310 | 77.5 | 60.6 | 47 | 28.3 | 28.3 | 2.2 | 2.2 | 39.5 | 39.4 | 39.5 | 39.4 | Dry | 35.9091 | 1240 | 29.7352 | 2.3865 | 41320.3261 | 38830.0029
2 | 475 | 77.2 | 60.3 | 46.9 | 27.5 | 27.6 | 3.2 | 3.2 | 56.5 | 56.5 | 56.5 | 56.5 | Dry | 35.3125 | 1900 | 28.567 | 3.3697 | 58267.5881 | 57203.1026
3 | 618 | 82.4 | 61.7 | 46.7 | 29.7 | 29.9 | 5.3 | 5.1 | 82.9 | 83.5 | 82.9 | 83.5 | Dry | 31.283 | 2472
4 | 381 | 93.6 | 66.1 | 46.7 | 42.9 | 42.4 | 4.8 | 4.5 | 74.1 | 70.2 | 74.1 | 70.2 | Dry | 30.875 | 1524
5 | 250 | 97.7 | 75.9 | 47.3 | 47.2 | 47.8 | 4.6 | 4.7 | 84.3 | 85.4 | 50.3 | 50.9 | Wet | 36.6522 | 1000
6 | 286 | 93.1 | 77.4 | 46.8 | 41.1 | 41.4 | 6.6 | 6.5 | 102.5 | 100.9 | 50.8 | 51.1 | Wet | 31.0606 | 1144
7 | 470 | 78.7 | 69.5 | 46.8 | 24.3 | 24 | 6.4 | 6.2 | 100.3 | 97.2 | 52.1 | 51.6 | Wet | 31.3437 | 1880
8 | 285 | 86.6 | 71 | 47.2 | 36.3 | 36.8 | 4.2 | 4.2 | 75 | 74.6 | 44 | 44.6 | Wet | 35.7143 | 1140
9 | 445 | 99 | 73.4 | 47.2 | 45 | 45.4 | 6.3 | 6.4 | 115.3 | 117.4 | 83 | 84.3 | Dry/Wet | 36.6032 | 1780
10 | 590 | 84.4 | 68 | 47.6 | 29.5 | 30.3 | 5.9 | 5.9 | 106.4 | 106.2 | 75 | 76.2 | Dry/Wet | 36.0678 | 2360
11 | 675 | 70.1 | 62.3 | 47.2 | 16.9 | 17.9 | 4.5 | 4.5 | 79.8 | 80.1 | 50 | 52.7 | Dry/Wet | 35.4667 | 2700
12 | 819 | 84.7 | 68.2 | 47.3 | 27.5 | 27.5 | 7.1 | 7.3 | 127.6 | 130.7 | 96.3 | 96 | Dry/Wet | 35.9437 | 3276 | 32.1808 | 7.4716 | 129539.4272 | 108938.1144

## Saturated Air Enthalpy
[8 empty] | Average Temp | 14
Temperature (C) | Temperature (F) | Saturated Partial Pressure (psia) | Saturated Humidity Ratio | Saturated Air Enthalpy (BTU/lb) | Saturated Air Enthalpy (J/kg) | (X - Xave) (Y-Yave) | (X - Xave)² | Average Enthalpy | 57834.0705
8 | 46.4 | 0.1556 | 0.0066557 | 18.3348 | 42646.7028 | 91124.2064 | 36 | a | 19927.6793 | J/kg
9 | 48.2 | 0.16652 | 0.007128 | 19.2833 | 44853.002 | 64905.3426 | 25 | b | 2707.5994 | J/kg-K
10 | 50 | 0.17811 | 0.00763 | 20.2648 | 47136.0217 | 42792.195 | 16
11 | 51.8 | 0.1904 | 0.0081635 | 21.2812 | 49500.0945 | 25001.9281 | 9
12 | 53.6 | 0.20343 | 0.0087301 | 22.3344 | 51949.7732 | 11768.5946 | 4
13 | 55.4 | 0.21724 | 0.0093316 | 23.4264 | 54489.843 | 3344.2275 | 1
14 | 57.2 | 0.23187 | 0.0099701 | 24.5595 | 57125.333 | 0 | 0
15 | 59 | 0.24735 | 0.010647 | 25.7358 | 59861.5289 | 2027.4584 | 1
16 | 60.8 | 0.26374 | 0.011366 | 26.9579 | 62703.9869 | 9739.8329 | 4
17 | 62.6 | 0.28108 | 0.012127 | 28.2281 | 65658.548 | 23473.4325 | 9
18 | 64.4 | 0.2994 | 0.012934 | 29.5492 | 68731.3536 | 43589.1323 | 16
19 | 66.2 | 0.31876 | 0.013789 | 30.9238 | 71928.8621 | 70473.9579 | 25
20 | 68 | 0.33921 | 0.014695 | 32.3551 | 75257.8668 | 104542.7778 | 36